DRAFT

DEPARTMENT OF FORESTRY & FIRE PROTECTION

OFFICE OF THE STATE FIRE MARSHAL

SPCC PLAN TEMPLATE FOR A TANK FACILITY WITH TANK(S) IN AN UNDERGROUND AREA & LESS THAN 1,320 GALLONS OIL STORAGE CAPACITY

Instructions to Complete this Template

This template is intended to help the owner or operator of a tank facility with one or more tanks in an underground area (TIUGA) develop a Spill Prevention, Control, and Countermeasure (SPCC) Plan. To use this template, the tank facility must have a total aggregate aboveground oil storage capacity of less than 1,320 gallons and have one or more TIUGAs as defined in the California Health and Safety Code (HSC) Section 25270.2(o)(1), excluding those specified in HSC Section 25270.3(c)(3).

Under the California Aboveground Petroleum Storage Act (APSA), a TIUGA must meet all the following:

- The storage tank is stationary (permanent or fixed installation).

- The storage tank is located on or above the surface of the floor in a structure at least 10 percent below the ground surface, including but not limited to, a basement, cellar, shaft, pit, or vault.

- The structure in which the storage tank is located must provide for secondary containment of the contents of the tank, piping, and ancillary equipment, until cleanup occurs.

- The structure in which the storage tank is located must allow for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor.2

- The storage tank meets one or more of the following categories:

  - Lubricant or coolant tank or oil-filled equipment: Contains petroleum (new or used oil) as lubricant or coolant in motor engines, transmissions, or oil-filled operational or manufacturing equipment (HSC Section 25270.2(o)(1)(C)(i)).

  - Hazardous waste tank: Contains petroleum that is considered a hazardous waste and complies with the hazardous waste tank standards in the California Code of Regulations (CCR), Title 22, Division 4.5, Chapter 15, Article 10 (HSC Section 25270.2(o)(1)(C)(ii)).

  - Emergency system: Contains petroleum to be used for emergency systems, solely in connection with a fire pump or an emergency system, legally required standby system, or optional standby system as defined in the California Electrical Code (HSC Section 25270.2(o)(1)(C)(iii)).

  - Other tank: Does not fit into any of the above three categories and contains petroleum (HSC Section 25270.2(o)(1)(C)(iv)).

Examples of storage tanks that are excluded or exempt from the APSA requirements of this template are as follows:

- A mobile or portable tank or container.

- A pressure vessel or boiler that is subject to Part 6 (commencing with Section 7620) of Division 5 of the Labor Code.

- A tank containing hazardous waste or extremely hazardous waste, as respectively defined in Sections 25117 and 25115, if the owner or operator of the storage tank has a hazardous waste facilities permit from the Department of Toxic Substances Control or a permit by rule authorization from the Unified Program Agency for the storage tank.

- Oil-filled electrical equipment, including, but not limited to, transformers, circuit breakers, or capacitors, if the oil-filled electrical equipment meets either of the following conditions:

  - The equipment contains less than 10,000 gallons of dielectric fluid.

  - The equipment contains 10,000 gallons or more of dielectric fluid with PCB levels less than 50 parts per million, appropriate containment or diversionary structures or equipment are employed to prevent discharged oil from reaching a navigable water course, and the electrical equipment is visually inspected in accordance with the usual routine maintenance procedures of the owner or operator.

- A TIUGA that has the capacity to store less than 55 gallons of petroleum.

- The tank holds hydraulic fluid for a closed loop mechanical system that uses compressed air or hydraulic fluid to operate lifts, elevators, or other similar devices.

- The tank is a heating oil tank.

- The tank is a sump, separator, clarifier, catch basin, or storm drain.

- The tank is permanently closed as defined in the Code of Federal Regulations (CFR), Title 40, Part 112, Section 112.2.

This template has been developed to meet the applicable requirements of HSC Chapter 6.67 and CFR Title 40, Part 112. The template is modeled after the U. S. Environmental Protection Agency (US EPA) Tier I Qualified Facility SPCC Plan template found in the CFR Title 40, Part 112, Appendix G, but has been modified to incorporate the APSA requirements for tank facilities that meet the criteria in HSC Section 25270.3(c).

The use of this template is not mandatory. This template may be used to comply with the APSA requirement to prepare an SPCC Plan as allowed under HSC Section 25270.4.5(c).

Complete this template either electronically or by hand on a printed copy. If completing this template electronically, be sure to save a copy on the computer before printing a hard copy. During an inspection by the local Unified Program Agency (UPA), the UPA inspector will want to review the printed, signed copy and associated records.

Each certifier of this template must complete Sections I, II, III, and IV. Complete and include with the SPCC Plan, the appropriate attachments. Consider printing copies of the attachments for use in implementing the SPCC Plan (e.g. Attachment 2.1 - Inspection Log & Schedule).

To complete this template, check the box next to the requirement to indicate that it has been adequately addressed. Either write “N/A” in the column or check the box under the “N/A” column to indicate those requirements that are not applicable to the tank facility. Where a section requires a description or listing, write in the spaces provided (or attach additional descriptions if more space is needed).

Below is a key for the colors used in the section headers:

Sections I, II, and III: General requirements for all tank facilities (with less than 1,320 gallons of oil and one or more TIUGAs)

Section IV: Specific requirements for all tank facilities (with less than 1,320 gallons of oil and one or more TIUGAs)

Attachments: 1 – Five Year Review and Technical Amendment Logs 2 – Inspections, Dike Drainage and Personnel Training Logs 3 – Release Notification Form

After completing all appropriate sections, certify and date the SPCC Plan, and then implement it. Conduct inspections and tests in accordance with the written procedures that have been developed for the tank facility. Keep with the SPCC Plan a record of these inspections and tests, signed by the appropriate supervisor or inspector, for a period of three years.

Do not forget to periodically review the SPCC Plan (at least once every five years) or to update it when making changes to the tank facility. Prepare amendments within six months of the tank facility change, and implement them as soon as possible, but not later than six months following preparation of any amendment.

In the event that the tank facility releases petroleum, immediately call the California Governor’s Office of Emergency Services (Cal OES) State Warning Center at (800) 852-7550 or (916) 845-8911 and the local UPA or 911. In addition, if the release reaches navigable water or adjoining shoreline, immediately call the National Response Center (NRC) at (800) 424-8802.

TIUGA Tank Facility SPCC Plan

This template constitutes the Spill Prevention, Control, and Countermeasure (SPCC) Plan for the tank facility when completed and signed by the owner or operator of a tank facility that meets the criteria in HSC §25270.3(c). This template addresses the applicable requirements of Health and Safety Code (HSC) Division 20, Chapter 6.67 (Aboveground Petroleum Storage Act (APSA)), Code of Federal Regulations (CFR) Title 40, Part 112, and the California Code of Regulations (CCR), Title 19, Division 1, Chapter 11. Maintain a complete copy of this SPCC Plan at the tank facility if the facility is normally attended at least four hours per day, or for a tank facility attended fewer than four hours per day, at the nearest field office. When making operational changes at a tank facility that are necessary to comply with the SPCC rule requirements, the owner or operator should follow state and local requirements (such as for permitting, design and construction) and obtain professional assistance, as appropriate.

# Tank Facility Description

| Tank Facility Name |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Tank Facility Address |  |  |  |  |  |
| City |  | State |  | ZIP |  |
| County |  | Telephone Number | ( ) - |  |  |
| Owner or Operator Name |  |  |  |  |  |
| Owner or Operator Address |  |  |  |  |  |
| City |  | State |  | ZIP |  |
| County |  | Telephone Number | ( ) - |  |  |

# I. Certification Statement (CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(1))

The owner or operator of a tank facility certifies that each of the following is true in order to utilize this template to comply with the SPCC requirements:

| I |  | certify that the following is accurate: |
| --- | --- | --- |

- I am familiar with the applicable requirements of CFR Title 40, Part 112, HSC Division 20, Chapter 6.67, and CCR Title 19, Division 1, Chapter 11;

- I have visited and examined the tank facility;

- This SPCC Plan was prepared in accordance with accepted and sound industry practices and standards;

- Procedures for required inspections and testing have been established in accordance with industry inspection and testing standards or recommended practices;

- I will fully implement this SPCC Plan;

- This tank facility meets the following qualification criteria (under HSC Section 25270.3(c)):

  - The aggregate aboveground oil storage capacity of the tank facility is less than 1,320 U.S. gallons; and

  - The tank facility has one or more tanks in an underground area (TIUGA) as defined in HSC Section 25270.2(o)(1), excluding those specified in HSC Section 25270.3(c)(3).

- This SPCC Plan does not deviate from any requirement of CFR Title 40, Part 112 as allowed by Section 112.7(a)(2) (environmental equivalence) and Section 112.7(d) (impracticability of secondary containment);

- This SPCC Plan and individual(s) responsible for implementing this SPCC Plan have the full approval of management, and I have committed the necessary resources to fully implement this SPCC Plan.

I also understand my other obligations relating to the storage of petroleum at this tank facility, including, among others:

- To report any petroleum release to navigable waters or adjoining shorelines to the appropriate authorities. Notification information is included in this SPCC Plan.

- To review and amend this SPCC Plan whenever there is a material change at the tank facility that affects the potential for a petroleum release, and at least once every five years. Reviews and amendments are recorded in an attached log [See Five Year Review Log and Technical Amendment Log in Attachments 1.1 and 1.2.]

I certify that I have satisfied the requirement to prepare and implement an SPCC Plan under HSC Section 25270.4.5(c) and all the applicable requirements under CFR Title 40, Part 112, HSC Chapter 6.67, and CCR Title 19, Division 1, Chapter 11. I certify that the information contained in this SPCC Plan is true.

| Signature |  | Title: |  |
| --- | --- | --- | --- |
| Name |  | Date: | / / 20 |

# II. Record of SPCC Plan Review and Amendments

# Five Year Review (CCR Title 19, Section #, ref. CFR Title 40, Section §112.5(b)):

Complete a review and evaluation of this SPCC Plan at least once every five years. As a result of the review, amend this SPCC Plan within six months to include more effective prevention and control measures for the tank facility, if applicable. Implement any SPCC Plan amendment as soon as possible, but no later than six months following the SPCC Plan amendment. Document completion of the review and evaluation, and complete the Five-Year Review Log in Attachment 1.1. If the tank facility’s no longer meets the criteria in HSC Section 25270.3(c) because the tank facility meets the criteria in HSC Section 25270.3(a) or (b), the owner or operator must complete a Tier I or Tier II qualified facility SPCC Plan, or complete a professional engineer (PE)-certified SPCC Plan.

| Table 1 Technical Amendments (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.5(a), (c) and 112.6(a)(2)) |  |
| --- | --- |
| This SPCC Plan will be amended when there is a change in the tank facility design, construction, operation, or maintenance that materially affects the potential for a release to navigable waters or adjoining shorelines. Examples include adding or removing storage tanks, reconstruction, replacement, or installation of piping systems, changes to secondary containment systems, changes in product stored at this tank facility, or revisions to standard operating procedures. |  |
| Any technical amendments to this SPCC Plan will be re-certified in accordance with Section I of this SPCC Plan template. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(2)] [See Technical Amendment Log in Attachment 1.2] |  |

# III. SPCC Plan Requirements

- Petroleum Storage Tanks (CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(a)(3)(i)):

| Table 2 Petroleum Storage Tanks and Capacities |  |  |  |  |
| --- | --- | --- | --- | --- |
| This table includes a complete list of all petroleum storage tanks (aboveground storage tanksa and completely buried tanksb) with capacity of 55 U.S. gallons or more, unless otherwise exempt from APSA. |  |  |  |  |
| Petroleum Storage Tank (indicate whether aboveground (A) or completely buried (B)) | Type of Petroleum | Shell Capacity (gallons) |  |  |
| Total Aboveground Storage Capacity c |  |  | gallons |  |
| Total Completely Buried Storage Capacity |  |  | gallons |  |
| Tank Facility Total Petroleum Storage Capacity |  |  | gallons |  |

a Tanks in an underground area that must be included when calculating total tank facility petroleum storage capacity include: storage tanks; oil-filled operational equipment; other oil-filled equipment, such as flow-through process equipment. Exempt or excluded containers or storage tanks that are not included in the capacity calculation include: any container or storage tank with a storage capacity of less than 55 gallons of petroleum; storage tanks used exclusively for wastewater treatment; permanently closed tanks; and heating oil storage tanks.

b Although the criteria to determine applicability for tank facilities focuses on the aboveground petroleum storage tanks at the tank facility, the completely buried tanks at a tank facility are still subject to the requirements and must be addressed in the template; however, they are not counted toward the tank facility applicability threshold.

c Counts toward tank facility applicability threshold.

- Secondary Containment and Spill Control (HSC Section 25270.2(o)(1)(B) and, if applicable, 25270.2(o)(1)(C)(iv)(IV), ref. CFR Title 40, Section 112.7(c):

| Table 3 Secondary Containment and Spill Control |  |
| --- | --- |
| The structure in which the storage tank is located, at a minimum, provides for secondary containment of the contents of the tank, piping, and ancillary equipment, until cleanup occurs. A shop-fabricated double-walled storage tank with a mechanical or electronic device used to detect leaks in the interstitial space meets the requirement for secondary containment of the contents of the tank. If applicable, except for an emergency vent that is solely designed to relieve excessive internal pressure, all piping connected to the tank, including any portion of a vent line, vapor recovery line, or fill pipe that is beneath the surface of the ground, and all ancillary equipment that is designed and constructed to contain petroleum, can either be visually inspected by direct viewing or has both secondary containment and leak detection. |  |

Table 4 below identifies the storage tanks at the tank facility with the potential for a petroleum release; the mode of failure; the flow direction and potential quantity of the release; and the secondary containment method and containment capacity that is provided.

| Table 4 Storage Tanks with Potential for a Petroleum Release |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Area | Type of failure (release scenario) | Potential release volume (gallons) | Direction of flow for uncontained release | Secondary containment methoda | Secondary containment capacity (gallons) |
| Storage Tanks |  |  |  |  |  |
| Oil-Filled Equipment (e.g., hydraulic equipment, lubricating systems) |  |  |  |  |  |
| Piping, Valves, etc. |  |  |  |  |  |
| Product Transfer Areas (location where petroleum is loaded to or from a storage tank, pipe or other piece of equipment) |  |  |  |  |  |

a Use one of the following methods of secondary containment or its equivalent: (1) Dikes, berms, or retaining walls sufficiently impervious to contain petroleum; (2) Curbing; (3) Culverting, gutters, or other drainage systems; (4) Weirs, booms, or other barriers; (5) Spill diversion ponds; (6) Retention ponds; or (7) Sorbent materials.

- Inspections, Testing, Recordkeeping and Personnel Training (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.7(e) and (f), and 112.8(c)(6) and (d)(4)):

| Table 5 Inspections, Testing, Recordkeeping and Personnel Training |  |  |
| --- | --- | --- |
| An inspection and/or testing program is implemented for all aboveground bulk storage tanks and piping at this tank facility. [CCR Title 19, Section #, ref. CFR Title 40, Sections 112.8(c)(6) and (d)(4)] |  |  |
| The following is a description of the inspection and/or testing program (e.g. reference to industry standard utilized, scope, frequency, method of inspection or test, and person conducting the inspection) for all aboveground bulk storage tanks and piping at this tank facility: |  |  |
| Inspections, tests, and records are conducted in accordance with written procedures developed for the tank facility. Records of inspections and tests kept under usual and customary business practices will suffice for purposes of this paragraph. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(e)] |  |  |
| A record of the inspections and tests are kept at the tank facility or with the SPCC Plan for a period of three years. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(e)] [See Inspection Log and Schedule in Attachment 2.1] |  |  |
| Inspections and tests are signed by the appropriate supervisor or inspector. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(e)] |  |  |
| Personnel, training, and release prevention procedures [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)] |  |  |
| Petroleum-handling personnel are trained in the operation and maintenance of equipment to prevent releases; release procedure protocols; applicable pollution control laws, rules, and regulations; general facility operations; and, the contents of the SPCC Plan. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)] |  |  |
| A person who reports to facility management is designated and accountable for release prevention. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)] |  |  |
| Name/Title: |  |  |
| Discharge prevention briefings are conducted for petroleum-handling personnel annually to assure adequate understanding of the SPCC Plan for that tank facility. Such briefings highlight and describe past reportable releases or failures, malfunctioning components, and any recently developed precautionary measures. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)] [See Petroleum-handling Personnel Training and Briefing Log in Attachment 2.4] |  |  |

4. Security (CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(g)):

| Table 6 Implementation and Description of Security Measures |  |
| --- | --- |
| Security measures are implemented at this tank facility to prevent unauthorized access to petroleum handling, processing, and storage area. |  |
| The following is a description of how you secure and control access to the petroleum handling, processing and storage areas; secure master flow and drain valves; prevent unauthorized access to starter controls on oil pumps; secure out-of-service and loading/unloading connections of petroleum pipelines; address the appropriateness of security lighting to both prevent acts of vandalism and assist in the discovery of petroleum releases: |  |

5. Emergency Procedures and Notifications (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.7(a)(3)(iv) and 112.7(a)(5)):

Table 7 Description of Emergency Procedures and Notifications

The following is a description of the immediate actions to be taken by tank facility personnel in the event of a release to navigable waters or adjoining shorelines [CCR Title 19, Section #, ref. CFR Title 40, Sections 112.7(a)(3)(iv) and 112.7(a)(5)]:

6. Contact List (CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(a)(3)(vi)):

| Table 8 Contact List |  |
| --- | --- |
| Contact Organization / Person | Telephone Number |
| National Response Center (NRC) | 1-800-424-8802 |
| Cleanup Contractor(s) |  |
| Key Facility Personnel |  |
| Designated Person Accountable for Release Prevention: | Office: |
|  | Emergency: |
|  | Office: |
|  | Emergency: |
|  | Office: |
|  | Emergency: |
|  | Office: |
|  | Emergency: |
| State Oil Pollution Control Agencies |  |
| Other State, Federal, and Local Agencies |  |
| Local Fire Department |  |
| Local Police Department |  |
| Hospital |  |
| Other Contact References (e.g., downstream water intakes or neighboring facilities) |  |

7. NRC Notification Procedure (CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(a)(4) and (a)(5)):

| Table 9 NRC Notification Procedure |  |  |
| --- | --- | --- |
| In the event of a release of petroleum to navigable waters or adjoining shorelines, the following information identified in Attachment 4 will be provided to the National Response Center immediately following identification of a release to navigable waters or adjoining shorelines [See Release Notification Form in Attachment 4]: [§112.7(a)(4)] |  |  |
| - The exact address or location and phone number of the tank facility; - Date and time of the release; - Type of material released; - Estimate of the total quantity released; - Estimate of the quantity released to navigable waters; - Source of the release; | - Description of all affected media; - Cause of the release; - Any damages or injuries caused by the release; - Actions being used to stop, remove, and mitigate the effects of the release; - Whether an evacuation may be needed; and - Names of individuals and/or organizations who have also been contacted. |  |

8. SPCC Spill Reporting Requirements (HSC Section 25270.8, CCR Title 19, Section #, ref. CFR Title 40, Section 112.4):

Submit information to the U.S. Environmental Protection Agency (US EPA) Regional Administrator (RA) and the appropriate agency or agencies in charge of oil pollution control activities in the State in which the tank facility is located from one of the following release events:

A single release of more than 1,000 U.S. gallons of petroleum to navigable waters or adjoining shorelines or

Two releases to navigable waters or adjoining shorelines each more than 42 U.S. gallons of petroleum occurring within any twelve-month period

You must submit the following information to the US EPA RA:

(1)	Name of the tank facility;

(2)	Tank facility owner or operator name;

(3)	Location of the tank facility;

(4)	Maximum storage or handling capacity of the tank facility and normal daily throughput;

(5)	Corrective action and countermeasures the owner or operator has taken, including a description of equipment repairs and replacements;

(6)	An adequate description of the tank facility, including maps, flow diagrams, and topographical maps, as necessary;

(7)	The cause of the reportable release, including a failure analysis of the system or subsystem in which the failure occurred; and

(8)	Additional preventive measures you have taken or contemplated to minimize the possibility of recurrence

(9)	Such other information as the US EPA Regional Administrator may reasonably require pertinent to the SPCC Plan or release

# NOTE: Complete one of the following sections (A, B or C)

as appropriate for the tank facility type.

# A. Onshore Tank Facilities (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.8(b) through (d), 112.12(b) through (d)):

The owner or operator must meet the general SPCC rule requirements as well as requirements under this section. Note that not all provisions may be applicable to all owners/operators. In cases where a provision is not applicable, write “N/A”.

| Table 10 General Rule Requirements for Onshore Tank Facilities |  | N/A |
| --- | --- | --- |
| Drainage from diked storage areas is restrained by valves to prevent a release into the drainage system or tank facility effluent treatment system, except where tank facility systems are designed to control such release. Diked areas may be emptied by pumps or ejectors that must be manually activated after inspecting the condition of the accumulation to ensure no petroleum will be released. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(b)(1)] |  |  |  |
| Valves of manual, open-and-closed design are used for the drainage of diked areas. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(b)(2)] |  |  |  |
| The storage tanks at the tank facility are compatible with materials stored and conditions of storage such as pressure and temperature. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(c)(1)] |  |  |  |
| Secondary containment for the bulk storage tanks holds the capacity of the largest storage tank. [ CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(3)(ii)] |  |  |  |
| If uncontaminated rainwater from diked areas drains into a storm drain or open watercourse the following procedures will be implemented at the tank facility: [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(c)(3)] |  |  |  |
| - Bypass valve is normally sealed closed |  |  |  |
| - Retained rainwater is inspected to ensure that its presence will not cause a release to navigable waters or adjoining shorelines |  |  |  |
| - Bypass valve is opened and resealed under responsible supervision |  |  |  |
| - Adequate records of drainage are kept [See Dike Drainage Log in Attachment 2.3] |  |  |  |
| Each storage tank is tested or inspected for integrity on a regular schedule and whenever material repairs are made. Scope and frequency of the inspections and inspector qualifications are in accordance with industry standards. Storage tank supports and foundations are regularly inspected. [See Inspection Log and Schedule and Bulk Storage Tank Inspection Schedule in Attachments 2.1 and 2.2] [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(c)(6)] |  |  |  |
| Outsides of storage tanks are frequently inspected for signs of deterioration, releases, or accumulation of petroleum inside diked areas. [See Inspection Log and Schedule in Attachment 2.1] [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(c)(6)] |  |  |  |
| Each storage tank is provided with a system or documented procedure to prevent overfills for the tank. Describe: |  |  |  |
| Liquid level sensing devices are regularly tested to ensure proper operation [See Inspection Log and Schedule in Attachment 2.1]. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(3)(iii)] |  |  |  |
| Visible releases which result in a loss of petroleum from the storage tank, including but not limited to seams, gaskets, piping, pumps, valves, rivets, and bolts are promptly corrected and petroleum in diked areas is promptly removed. [CCR Title 19, Sections #, ref. CFR Title 40, Section 112.8(c)(10)] |  |  |  |
| Aboveground valves, piping, and appurtenances such as flange joints, expansion joints, valve glands and bodies, catch pans, pipeline supports, locking of valves, and metal surfaces are inspected regularly. [See Inspection Log and Schedule in Attachment 2.1] [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(d)(4)] |  |  |  |
| Integrity and leak testing are conducted on buried piping at the time of installation, modification, construction, relocation, or replacement. [See Inspection Log and Schedule in Attachment 2.1] [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(d)(4)] |  |  |  |

ATTACHMENT 1.1 – Five-Year Review Log

ATTACHMENT 1 – Five-Year Review and Technical Amendment Logs

The owner or operator has completed a review and evaluation of the SPCC Plan for this tank facility, and will/will not amend this SPCC Plan as a result.

| Table 11 Review and Evaluation of SPCC Plan for Tank Facility |  |  |  |
| --- | --- | --- | --- |
| Review Date | SPCC Plan Amendment |  | Name and signature of person authorized to review this SPCC Plan |
|  | Will Amend | Will Not Amend |  |
| Description of changes/amendments: |  |  |  |
| Description of changes/amendments: |  |  |  |
| Description of changes/amendments: |  |  |  |
| Description of changes/amendments: |  |  |  |
| Description of changes/amendments: |  |  |  |

ATTACHMENT 1.2 – Technical Amendment Log

| Any technical amendments to this SPCC Plan will be re-certified in accordance with Section I of this SPCC Plan template. |  |  |
| --- | --- | --- |
| Table 12 Description and Certification of Technical Amendments |  |  |
| Review Date | Description of Technical Amendment | Name and signature of person certifying this technical amendment |

# ATTACHMENT 2 – Inspections, Dike Drainage and Personnel Training Logs

# ATTACHMENT 2.1 – Inspection Log and Schedule

| Table 13 Inspection Log and Schedule This log is intended to document compliance with CCR Title 19, Sections #, ref. CFR Title 40, Sections 112.6(a)(3)(iii), 112.8(c)(6), 112.8(d)(4), as applicable. |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Date of Inspection | Storage tank / Piping / Equipment | Describe Scope (or cite Industry Standard) | Observations | Name/ Signature of Inspector | Records maintained separately a |

a Indicate in the table above if records of tank facility inspections are maintained separately for this tank facility.

ATTACHMENT 2.2 – Bulk Storage Tank Inspection Schedule – onshore facilities (excluding production):

To comply with integrity inspection requirement for bulk storage tanks, inspect/test each shop-built aboveground bulk storage tank on a regular schedule in accordance with a recognized storage tank inspection standard based on the minimum requirements in the following table.

| Table 14 Bulk Storage Tank Inspection Schedule |  |
| --- | --- |
| Storage Tank Size and Design Specification | Inspection requirement |
| 55 to 1,100 gallons with sized secondary containment | Visually inspect monthly for signs of deterioration, releases or accumulation of petroleum inside diked areas plus any annual inspection elements per industry inspection standards |
| 1,101 to 1,319 gallons with sized secondary containment and a means of leak detectiona |  |
| 1,101 to 1,319 gallons with sized secondary containment and no method of leak detectiona | Visually inspect monthly for signs of deterioration, releases or accumulation of petroleum inside diked areas, plus any annual inspection elements and other specific integrity tests that may be required per industry inspection standards |

a Examples of leak detection include, but are not limited to, double-walled tanks and elevated storage tanks where a leak can be visually identified.

| Table 15 Dike Drainage Log |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Date | Bypass valve sealed closed | Rainwater inspected to be sure no petroleum (or sheen) is visible | Open bypass valve and reseal it following drainage | Drainage activity supervised | Observations | Signature of Inspector |

# ATTACHMENT 2.3 – Dike Drainage Log

| Table 16 Petroleum-Handling Personnel Training and Briefing Log |  |  |
| --- | --- | --- |
| Date | Description / Scope | Attendees |

ATTACHMENT 2.4 – Petroleum-handling Personnel Training and Briefing Log

| In the event of a release of petroleum to navigable waters or adjoining shorelines, the following information will be provided to the National Response Center [also see the notification information provided in item 7 of section III of this SPCC Plan]: |  |  |  |
| --- | --- | --- | --- |
| Table 17 Information Provided to the National Response Center in the Event of a Release |  |  |  |
| Release/Discovery Date |  | Time |  |
| Tank Facility Name |  |  |  |
| Tank Facility Location (Address/Lat-Long/Section Township Range) |  |  |  |
| Name of reporting individual |  | Telephone # |  |
| Type of material released |  | Estimated total quantity released | Gallons/Barrels |
| Source of the release |  | Media affected | Soil |
|  |  |  | Water (specify) |
|  |  |  | Other (specify) |
| Actions taken |  |  |  |
| Damage or injuries | No Yes (specify) | Evacuation needed? | No Yes (specify) |
| Organizations and individuals contacted | National Response Center 800-424-8802 Time |  |  |
|  | Cleanup contractor (Specify) Time |  |  |
|  | Tank facility personnel (Specify) Time |  |  |
|  | State Agency (Specify) Time |  |  |
|  | Other (Specify) Time |  |  |

# ATTACHMENT 3 – Release Notification Form