


[image: ]

DRAFT
DEPARTMENT OF FORESTRY & FIRE PROTECTION
OFFICE OF THE STATE FIRE MARSHAL
SPCC PLAN TEMPLATE FOR A TANK FACILITY WITH TANK(S) IN AN UNDERGROUND AREA AND LESS THAN 1,320 GALLONS OIL STORAGE CAPACITY

Instructions to Complete this Template
This template is intended to help the owner or operator of a tank facility with one or more tanks in an underground area (TIUGA) develop a Spill Prevention, Control, and Countermeasure (SPCC) Plan. To use this template, the tank facility must have a total aggregate aboveground oil (petroleum or non-petroleum, waste or product) storage capacity less than 1,320 gallons, and have one or more TIUGAs as defined in the California Health and Safety Code (HSC) Section 25270.2(o)(1), excluding those specified in HSC Section 25270.3(c)(3). Examples of oil tanks and containers to be counted toward the 1,320-gallon determination are any of the following, provided they have a 55-gallon or greater shell capacity:
· Stationary tanks (permanent or fixed installation, or originally designed or manufactured for use as a stationary tank)
· A mobile or portable tank or container (drums, intermediate bulk containers, or totes)
· Oil-filled electrical equipment, including, but not limited to, transformers, circuit breakers, or capacitors
· Oil-filled manufacturing or operational equipment (including hydraulic systems and machining reservoirs)
· Mobile refuelers and oilers
· Heating oil tanks that are not used at a single-family residence
If the tank facility has a total aggregate storage capacity of more than 1,320 gallons of oil (including petroleum) in any 55-gallon or larger aboveground storage tank, container, oil-filled equipment, or mobile refueler, then the owner or operator cannot use this template.
Note: Certified Unified Program Agency (CUPA)-permitted underground storage tanks (UST) are excluded from APSA. 
Under the California Aboveground Petroleum Storage Act (APSA), a TIUGA must meet ALL the following:
· The storage tank contains petroleum. AND
· The storage tank is stationary (permanent or fixed installation). AND
· The storage tank is located on or above the surface of the floor in a structure at least 10 percent below the ground surface, including but not limited to, a basement, cellar, shaft, pit, or vault. AND
· The structure in which the storage tank is located must provide for secondary containment of the contents of the tank, piping, and ancillary equipment, until cleanup occurs. AND
· The structure in which the storage tank is located must allow for direct viewing of the exterior of the tank except for the part of the tank in contact with the surface of the floor.
Once the facility has calculated the total oil capacity and verified it is under 1,320 gallons, then in completing this template, the facility should not include the following storage tanks that are exempt or excluded from the definition of a TIUGA.
· A mobile or portable tank or container.
· A pressure vessel or boiler that is subject to Part 6 (commencing with Section 7620) of Division 5 of the Labor Code.
· A tank containing hazardous waste or extremely hazardous waste, as respectively defined in Sections 25117 and 25115, if the owner or operator of the storage tank has a hazardous waste facilities permit from the Department of Toxic Substances Control or a permit by rule authorization from the Unified Program Agency for the storage tank.
· Oil-filled electrical equipment, including, but not limited to, transformers, circuit breakers, or capacitors, if the oil-filled electrical equipment meets either of the following conditions:
· The equipment contains less than 10,000 gallons of dielectric fluid.
· The equipment contains 10,000 gallons or more of dielectric fluid with PCB levels less than 50 parts per million, appropriate containment or diversionary structures or equipment are employed to prevent discharged oil from reaching a navigable water course, and the electrical equipment is visually inspected in accordance with the usual routine maintenance procedures of the owner or operator.
· A tank that has a shell capacity of less than 55 gallons of petroleum.
· The tank holds hydraulic fluid for a closed loop mechanical system that uses compressed air or hydraulic fluid to operate lifts, elevators, or other similar devices.
· A heating oil tank.
· The tank is a sump, separator, clarifier, catch basin, or storm drain.
· The tank is permanently closed as defined in the Code of Federal Regulations (CFR), Title 40, Part 112, Section 112.2. 
This template may be used to comply with the APSA requirement to prepare an SPCC Plan as allowed under HSC Section 25270.4.5(c). The use of this template is optional. If the template is not used, an SPCC Plan must be prepared in accordance with HSC Section 25270.4.5(a). 
Complete this template either electronically or by hand on a printed copy. If completing this template electronically, be sure to save a copy on the computer before printing a hard copy. During an inspection by the local Certified Unified Program Agency (CUPA), the CUPA inspector will want to review the printed, signed copy and associated records.
To complete this template, check the box next to the requirement to indicate that it has been adequately addressed. Either write “N/A” in the column or check the box under the “N/A” column to indicate those requirements that are not applicable to the tank facility. Where a section requires a description or listing, write in the spaces provided (or attach additional descriptions if more space is needed).
After completing this template, certify and date the SPCC Plan, and then implement it. Conduct inspections and tests in accordance with the written procedures that have been developed for the tank facility. Keep with the SPCC Plan a record of these inspections and tests, signed by the appropriate supervisor or inspector, for a period of three years.
Consider printing copies of the attachments for use in implementing the SPCC Plan (e.g. Attachment 2.1 - Inspection Log & Schedule). 
Do not forget to periodically review the SPCC Plan (at least once every five years) or to update it when making changes to the tank facility. Prepare amendments within six months of the tank facility change, and implement them as soon as possible, but not later than six months following preparation of any amendment.
In the event the tank facility releases petroleum that poses a threat or potential threat to health, safety, and the environment, immediately call the California Governor’s Office of Emergency Services (Cal OES) State Warning Center at (800) 852-7550 and (either or both) the local CUPA or 911. In addition, if the release reaches navigable water or adjoining shoreline, immediately call the National Response Center (NRC) at (800) 424-8802.

TIUGA Tank Facility SPCC Plan 

This template constitutes the Spill Prevention, Control, and Countermeasure (SPCC) Plan for the tank facility when completed and signed by the owner or operator of a tank facility that meets the criteria in HSC §25270.3(c). This template addresses the applicable requirements of Health and Safety Code (HSC) Division 20, Chapter 6.67 (Aboveground Petroleum Storage Act (APSA)), Code of Federal Regulations (CFR) Title 40, Part 112, and the California Code of Regulations (CCR), Title 19, Division 1, Chapter 11. Maintain a complete copy of this SPCC Plan at the tank facility if the facility is normally attended at least four hours per day, or for a tank facility attended fewer than four hours per day, at the nearest field office. When making operational changes at a tank facility that are necessary to comply with the SPCC rule requirements, the owner or operator should follow state and local requirements (such as for permitting, design and construction) and obtain professional assistance, as appropriate.
[bookmark: _Toc228869358][bookmark: _Toc230692314][bookmark: _Toc233536877][bookmark: _Toc243722628][bookmark: _Toc244321228]Tank Facility Description
Tank Facility Name:      
Tank Facility Address:      
City:      		State: CA	Zip Code:      
County:      	Phone Number:      
Owner or Operator Name:      
Owner or Operator Address:      
City:      		State: CA	Zip Code:       
County:      	Phone Number:      

[bookmark: _Toc228869359][bookmark: _Toc230692315][bookmark: _Toc233536878][bookmark: _Toc243722629][bookmark: _Toc244321229]I. Certification Statement (CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(1))
The owner or operator of a tank facility certifies that each of the following is true in order to utilize this template to comply with the SPCC requirements:

I ____________________________ , the owner or operator, certify that the following is accurate: 

1. I am familiar with the applicable requirements of HSC Division 20, Chapter 6.67, and CCR Title 19, Division 1, Chapter 11;
2. I have visited and examined the tank facility;
3. This SPCC Plan was prepared in accordance with accepted and sound industry practices and standards;
4. I will fully implement this SPCC Plan, including inspections, testing, training, and plan reviews;
5. This tank facility meets the following criteria (under HSC Section 25270.3(c)):
a. The aggregate aboveground oil storage capacity of the tank facility is less than 1,320 U.S. gallons; and
b. The tank facility has one or more tanks in an underground area (TIUGA) as defined in HSC Section 25270.2(o)(1), excluding those specified in HSC Section 25270.3(c)(3).
6. This SPCC Plan and individual(s) responsible for implementing this SPCC Plan have the full approval of management, and I have committed the necessary resources to fully implement this SPCC Plan.

I also understand my other obligations relating to the storage of petroleum at this tank facility, including, among others: 

1. To report any petroleum releases to the appropriate authorities as required. Notification information is included in this SPCC Plan.
2. To review and amend this SPCC Plan whenever there is a material change at the tank facility that affects the potential for a petroleum release, and at least once every five years. Reviews and amendments are recorded in an attached log [See Five-Year Review Log and Technical Amendment Log in Attachments 1.1 and 1.2.]
3. To maintain a complete copy of this SPCC Plan at the tank facility if the facility is normally attended at least four hours per day, or at the nearest field office if the facility is not so attended.

I certify that I have satisfied the requirement to prepare and implement an SPCC Plan under HSC Section 25270.4.5(c) and all the applicable requirements under HSC Division 20, Chapter 6.67, and CCR Title 19, Division 1, Chapter 11. I certify that the information contained in this SPCC Plan is true.

Signature: ___________________________________

Name:       
Title:      		Date:      



[bookmark: _Toc228869360][bookmark: _Toc230692316][bookmark: _Toc233536879][bookmark: _Toc243722630][bookmark: _Toc244321230]
II. Record of SPCC Plan Review and Amendments
[bookmark: _Toc228869361][bookmark: _Toc230692317][bookmark: _Toc233536880][bookmark: _Toc243722631][bookmark: _Toc244321231]Five-Year Review (CCR Title 19, Section #, ref. CFR Title 40, Section §112.5(b))
Complete a review and evaluation of this SPCC Plan at least once every five years. Document completion of the review and evaluation, and complete the Five-Year Review Log in Attachment 1.1. 
As a result of the review, amend this SPCC Plan within six months to include more effective prevention and control measures for the tank facility, if applicable. 
Implement any SPCC Plan amendment as soon as possible, but no later than six months following the SPCC Plan amendment. 
If the tank facility no longer meets the criteria in HSC Section 25270.3(c) because the tank facility meets the criteria in HSC Section 25270.3(a) or (b), the owner or operator must complete a Tier I or Tier II qualified facility SPCC Plan, or complete a professional engineer (PE)-certified SPCC Plan.  The new plan must be completed before beginning operation (e.g., filling) of the new storage tank(s), containers, mobile refuelers, or oil-filled equipment. 
Table 1 Technical Amendments (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.5(a), (c) and 112.6(a)(2))
	This SPCC Plan will be amended when there is a change in the tank facility design, construction, operation, or maintenance that materially affects the potential for a release to navigable waters or adjoining shorelines. Examples include adding or removing storage tanks, reconstruction, replacement, or installation of piping systems, changes to secondary containment systems, changes in product stored at this tank facility, or revisions to standard operating procedures.
	|_|

	Any technical amendments to this SPCC Plan will be re-certified in accordance with Section I of this SPCC Plan template. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(2)] [See Technical Amendment Log in Attachment 1.2]
	|_|


[bookmark: _Toc228869362][bookmark: _Toc230692318][bookmark: _Toc233536881][bookmark: _Toc243722632][bookmark: _Toc244321232]
III. SPCC Plan Requirements 
1. Tanks in Underground Areas (CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(a)(3)(i)):
Table 2 below includes a complete list of each tank in an underground area (TIUGA) with a shell capacity of 55 U.S. gallons or more. 

Examples of TIUGAs that must be listed are: (permanent or fixed) storage tanks, including day tanks; oil-filled operational or manufacturing equipment. 

Do not list storage tanks that are not TIUGAs. Refer to instructions for additional clarification. 

Add additional pages, if necessary.

Table 2 Petroleum Storage Tanks and Capacities
	Petroleum Storage Tank
	Type of Petroleum
	Shell Capacity (gallons)

	[bookmark: Text22]     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     


Total Aboveground Petroleum Storage Capacity (gallons):      



2. Secondary Containment and Spill Control (HSC Section 25270.2(o)(1)(B) and, if applicable, 25270.2(o)(1)(C)(iv)(IV), ref. CFR Title 40, Section 112.7(c):
Table 3 Secondary Containment and Spill Control
	The structure in which the storage tank is located, at a minimum, provides for secondary containment of the contents of the tank, piping, and ancillary equipment, until cleanup occurs. 
	Yes |_| N/A |_|

	Additional secondary containment methods used for TIUGA systems, if applicable:
	

	· Double walled tank where interstitial space is inspected by direct viewing
	Yes |_| N/A |_|

	· Double walled tank where interstitial space is monitored by mechanical or electronic leak detection device
	Yes |_| N/A |_|

	· Single walled tank with active secondary containment measures (spill response absorbents etc.)
	Yes |_| N/A |_|

	· Single walled tank inside containment (curb, berm, etc.)
	Yes |_| N/A |_|

	· Active secondary containment measures such as spill kit and response measures for transfer areas (filling of tank etc.)
	Yes |_| N/A |_|

	All piping connected to the tank, including the vent line, vapor recovery line, or fill pipe, and all ancillary equipment, can either be visually inspected by: 
	

	· Direct viewing or 
	Yes |_| N/A |_|

	· Has both secondary containment and leak detection

Note: This does not apply to an emergency vent that is solely designed to relieve excessive internal pressure.  This also does not apply to any TIUGA that meets one or more of the following: 
· Lubricant or coolant (petroleum) tank or oil-filled equipment (HSC Section 25270.2(o)(1)(C)(i)).
· Hazardous waste/used oil tank that complies with the hazardous waste tank standards in the California Code of Regulations (CCR), Title 22, Division 4.5, Chapter 15, Article 10 (HSC Section 25270.2(o)(1)(C)(ii)).
· Emergency system tank connected to a fire pump or an emergency generator (legally required or optional standby system as defined in the California Electrical Code) (HSC Section 25270.2(o)(1)(C)(iii)).
	Yes |_| N/A |_|
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Complete Table 4 below, identifying the TIUGAs listed in Table 1 at the tank facility and their associated potential for a petroleum release; the mode of failure; the flow direction and potential quantity of the release; and the secondary containment method and containment capacity that is provided.  Add additional pages, if necessary.  

Table 4 Storage Tanks with Potential for a Petroleum Release
	Tank System (includes the tank or oil-filled equipment plus any connected piping and valves) 
	Type of failure (release scenario)
	Potential release volume (gallons)
	Direction of flow for uncontained release
	Secondary containment capacity (gallons)

	     
	Complete rupture of the tank
	     
	     
	     

	
	Overfill
	     
	     
	     

	
	Piping or valve connection weep or leak
	     
	     
	     

	
	Petroleum Transfer Area
	     
	     
	     

	
	Other:      
	     
	     
	     

	     
	Complete rupture of the tank
	     
	     
	     

	
	Overfill
	     
	     
	     

	
	Piping or valve connection weep or leak
	     
	     
	     

	
	Petroleum Transfer Area
	     
	     
	     

	
	Other:      
	     
	     
	     

	     
	Complete rupture of the tank
	     
	     
	     

	
	Overfill
	     
	     
	     

	
	Piping or valve connection weep or leak
	     
	     
	     

	
	Petroleum Transfer Area
	     
	     
	     

	
	Other:      
	     
	     
	     

	     
	Complete rupture of the tank
	     
	     
	     

	
	Overfill
	     
	     
	     

	
	Piping or valve connection weep or leak
	     
	     
	     

	
	Petroleum Transfer Area
	     
	     
	     

	
	Other:      
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3. Inspections, Testing, Recordkeeping and Personnel Training (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.7(e) and (f), and 112.8(c)(6) and (d)(4)):
Table 5 Inspections, Testing, Recordkeeping and Personnel Training
	A monthly and annual inspection and/or testing program is implemented for all TIUGAs and connected piping at this tank facility. Inspector qualifications are in accordance with industry standards. Storage tank supports and foundations are regularly inspected.  [CCR Title 19, Section #, ref. CFR Title 40, Sections 112.8(c)(6) and (d)(4)] [Complete Monthly and Annual Inspection Logs in Attachment 2.1]
	|_|

	A record of the inspections and tests are kept at the tank facility or with the SPCC Plan for at least three years (hardcopy or electronic). [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(e)] [Complete Monthly and Annual Inspection Logs in Attachment 2.1]
	|_|

	Inspections and tests are signed by the appropriate supervisor or inspector. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(e)]
	|_|

	Personnel, training, and release prevention procedures [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)]
	

	Petroleum-handling personnel have received initial training in the operation and maintenance of equipment to prevent releases; release procedure protocols; applicable pollution control laws, rules, and regulations; general facility operations; and the contents of this SPCC Plan. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)]
[See Petroleum-handling Personnel Training and Briefing Log in Attachment 2.4]
	|_|

	Annual spill/discharge prevention briefings are conducted for petroleum-handling personnel to assure adequate understanding of this SPCC Plan. Such briefings highlight and describe past releases or failures, malfunctioning components, and any new spill prevention measures. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)] 
[See Petroleum-handling Personnel Training and Briefing Log in Attachment 2.4] 
	|_|

	A person who reports to facility management is designated and accountable for release prevention. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(f)]
	|_|

	Name/Title:
	[bookmark: Text27]     
	


4. 
Security (CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(g)):

	The following security measures are implemented at this tank facility to prevent unauthorized access or acts of vandalism to the TIUGAs.
· Controlled access to facility (locked door, fencing, gates, etc.)
· Controlled access to TIUGA (locked pump controls, remote fills/fill boxes, tank room)
· Security lighting
· Security cameras
· Other:      
	
|_|
|_|
|_|
|_|
|_|



5. Emergency Procedures, Notification, and Contact list (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.7(a)(3)(iv),(vi) and 112.7(a)(5)):

	The facility has a current Hazardous Materials Business Plan submitted to the California Environmental Reporting System (CERS). [HSC Section § 25270.6(a), CCR Title 19, Section #, ref. CFR Title 40, Sections 112.7(a)(3)(iv) and 112.7(a)(5)]:
	
|_|


	The Hazardous Materials Business Plan is readily available to facility personnel.
	|_|




6. Notification Procedure (CCR Title 19, Section #, ref. CFR Title 40, Section 112.7(a)(4) and (a)(5)):

	In the event of a reportable release of petroleum, the following information will be provided to the California Governor’s Office of Emergency Services (Cal OES), the CUPA, and, if necessary, 911. Immediate reporting is required for releases and threatened releases posing a significant present or potential hazard to human health and safety, property, or the environment. [CFR Title 40, §112.7(a)(4)] (HSC §25507(a) and Title 19 California Code of Regulations ([19 CCR] 2631)
	|_|


· The exact address or location and phone number of the tank facility; 
· Date and time of the release; 
· Type of material released; 
· Estimate of the total quantity released; 
· Estimate of the quantity released to navigable waters; 
· Source of the release;
· Description of all affected media; 
· Cause of the release; 
· Any damages or injuries caused by the release; 
· Actions being used to stop, remove, and mitigate the effects of the release; 
· Whether an evacuation may be needed; and
· Names of individuals and/or organizations who have also been contacted.

The California Hazardous Materials Spill/Release Notification Guidance booklet is available from the Cal OES website.



8. Additional Petroleum Spill Reporting Requirements (CCR Title 19, Section #, ref. CFR Title 40, Section #):
Immediately report to the National Response Center (NRC) (800-424-8802) any release of petroleum to a navigable waterway or adjoining shorelines. Complete the NRC reporting form in Attachment 3.
A. Onshore Tank Facilities (CCR Title 19, Section #, ref. CFR Title 40, Sections 112.8(b) through (d), 112.12(b) through (d)):

The owner or operator must meet the general SPCC rule requirements as well as requirements under this section. In cases where a provision is not applicable, mark “N/A”.

Table 6 General Rule Requirements for Onshore Tank Facilities
	Drainage from diked storage areas is restrained by valves to prevent a release into the drainage system or tank facility effluent treatment system, except where tank facility systems are designed to control such release.  Diked areas may be emptied by pumps or ejectors that must be manually activated after inspecting the condition of the accumulation to ensure no petroleum will be released. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(b)(1)]
	Yes |_| N/A |_|

	Valves of manual, open-and-closed design are used for the drainage of diked areas. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(b)(2)]
	Yes |_| N/A |_|

	The storage tanks at the tank facility are compatible with materials stored and conditions of storage such as pressure and temperature. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(c)(1)]
	Yes |_| N/A |_|

	Secondary containment for the bulk storage tanks holds the capacity of the largest storage tank. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(3)(ii)] 
	Yes |_| N/A |_|

	
If uncontaminated rainwater from diked areas drains into a storm drain or open watercourse, the following procedures will be implemented at the tank facility: [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(c)(3)]
	

	· Bypass valve is normally sealed closed

	Yes |_| N/A |_|

	· Retained rainwater is inspected to ensure that its presence will not cause a release to navigable waters or adjoining shorelines

	Yes |_| N/A |_|

	· Bypass valve is opened and resealed under responsible supervision

	Yes |_| N/A |_|

	· Adequate records of drainage are kept [See Dike Drainage Log in Attachment 2.3]
	Yes |_| N/A |_|

	Each storage tank is provided with a system or documented procedure to prevent overfills for the tank. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(3)(iii), 112.8(c)(8)(i)] 

· High liquid level alarms with an audible or visual signal at a constantly attended operation or surveillance station. 

· High liquid level pump cutoff devices set to stop flow at a predetermined container content level.

· Direct audible or code signal communication between the container gauger and the filling source/location.

· A fast response system for determining the liquid level of each bulk storage container such as digital computers, telepulse, or direct vision gauges. If you use this alternative, a person must be present to monitor gauges and the overall filling of bulk storage containers.

· Other (Describe):      
	



Yes |_| N/A |_|


Yes |_| N/A |_|


Yes |_| N/A |_|


Yes |_| N/A |_|




Yes |_| N/A |_|

	Liquid level sensing devices are regularly tested to ensure proper operation [See Inspection Log and Schedule in Attachment 2.1]. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.6(a)(3)(iii)] 
	Yes |_| N/A |_|

	Visible releases which result in a loss of petroleum from the storage tank, including but not limited to: seams, gaskets, piping, pumps, valves, rivets, and bolts, are corrected. 
[CCR Title 19, Sections #, ref. CFR Title 40, Section 112.8(c)(10)]
	Yes |_| N/A |_|

	Promptly remove petroleum accumulation from fill boxes, diked, bermed, curbed, and other containment areas.
[CCR Title 19, Sections #, ref. CFR Title 40, Section 112.8(c)(10)]
	Yes |_| N/A |_|

	Aboveground valves, piping, and appurtenances such as flange joints, expansion joints, valve glands and bodies, catch pans, pipeline supports, locking of valves, and metal surfaces are inspected regularly. [See Inspection Log and Schedule in Attachment 2.1] [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(d)(4)]
	Yes |_| N/A |_|

	Integrity and leak testing are conducted on buried piping at the time of installation, modification, construction, relocation, or replacement. Records of this integrity and leak testing must be retained for at least three years. [CCR Title 19, Section #, ref. CFR Title 40, Section 112.8(d)(4)]
	Yes |_| N/A |_|
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[bookmark: _Toc228869365][bookmark: _Toc230692321][bookmark: _Toc233536884][bookmark: _Toc243722635][bookmark: _Toc244321235]ATTACHMENT 1 – Five-Year Review and Technical Amendment Logs
ATTACHMENT 1.1 – Five-Year Review Log
The owner or operator has completed a review and evaluation of the SPCC Plan for this tank facility, and will/will not amend this SPCC Plan as a result.  Add additional pages, if necessary.
	Review Date
	SPCC Plan Amendment
	Name and Signature of Person Authorized to Review this SPCC Plan
	Description of Changes or Amendments

	     
	|_| Will Amend     |_| Will Not Amend
	     
	     

	     
	|_| Will Amend     |_| Will Not Amend
	     
	     

	     
	|_| Will Amend     |_| Will Not Amend
	     
	     

	     
	|_| Will Amend     |_| Will Not Amend
	     
	     




ATTACHMENT 1.2 – Technical Amendment Log
Any technical amendments to this SPCC Plan will be re-certified in accordance with Section I of this SPCC Plan template.  Add additional pages, if necessary. 
	Review Date
	Description of Technical Amendment
	Name and Signature of Person Certifying this Technical Amendment

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     




[bookmark: _Toc228869368][bookmark: _Toc230692324][bookmark: _Toc233536887][bookmark: _Toc243722638][bookmark: _Toc244321238]ATTACHMENT 2 – Inspections, Dike Drainage and Personnel Training Logs
This log is intended to document compliance with CCR Title 19, Sections #, ref. CFR Title 40, Sections 112.6(a)(3)(iii), 112.8(c)(6), 112.8(d)(4), as applicable.

ATTACHMENT 2.1 – Inspection Logs
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Insert monthly and annual checklists here





ATTACHMENT 2.2 – Bulk Storage Tank Inspection Schedule – onshore facilities (excluding production):

To comply with integrity inspection requirement for bulk storage tanks, inspect/test each shop-built aboveground bulk storage tank on a regular schedule in accordance with a recognized storage tank inspection standard based on the minimum requirements: 

Visually inspect monthly and annually for signs of deterioration, releases or accumulation of petroleum inside diked areas or secondary containment. Use the monthly and annual checklists in this template.
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	Date
	Drainage valve sealed closed
	Rainwater inspected to be sure no petroleum (or sheen) is visible
	Open drainage valve and reseal it following drainage
	Drainage activity supervised
	Observations
	Signature of Inspector

	     
	|_|
	|_|
	|_|
	|_|
	     
	

	     
	|_|
	|_|
	|_|
	|_|
	     
	

	     
	|_|
	|_|
	|_|
	|_|
	     
	

	     
	|_|
	|_|
	|_|
	|_|
	     
	

	     
	|_|
	|_|
	|_|
	|_|
	     
	


ATTACHMENT 2.3 – Dike Drainage Log
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	Date
	Description / Scope
	Attendees

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     

	     
	     
	     


[bookmark: _Toc228869371][bookmark: _Toc230692327][bookmark: _Toc233536890][bookmark: _Toc243722641][bookmark: _Toc244321241]ATTACHMENT 2.4 – Petroleum-handling Personnel Training and Briefing Log
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ATTACHMENT 3 – Release Notification Form

In the event of a release of petroleum to navigable waters or adjoining shorelines, the following information will be provided to the National Response Center [also see the notification information provided in item 7 of section III of this SPCC Plan]:

Release/Discovery Date:      	Time:      
Tank Facility Name:      
Tank Facility Location (Address/Lat-Long/Section Township Range):      
Name of Reporting Individual:      	Phone Number:      
Type of Material Released:      
Estimated Total Quantity Released:      
Source of Release:      
Media Affected: 
|_| Soil
|_| Water (specify)       
|_| Other (specify)      
Actions Taken:      
Damage or Injuries?
|_| No
|_| Yes (specify)      
Evacuation Needed? 
|_| No
|_| Yes (specify)      
Organizations and Individuals Contacted:
|_| National Response Center 800-424-8802	Time      
|_| Cleanup Contractor (Specify)      	Time      
|_| Tank Facility Personnel (Specify)      	Time      
|_| State Agency (Specify)      	Time      
|_| Other (Specify)      	Time      
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